## HPSEB Config
CONFIGURATION FORMAT

set Display Parameter
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	6	WSETDP	ASCII
10	Display Mode	1	0 or 1	ASCII
11	No of Parameters	2	1 to 60	ASCII	max can be set 60
13	Display Para Ids	120	0 to FF as ASCII	ASCII	List of Ids will be provided.
					pad zero if parameters are less than 60
					to make it 120 bytes
133	Crc of Configuration	4	0 to FF	ASCII	crc of configuration para meter will start from 11th byte to 132nd bytes
					lower bytes first.
137	End bytes	2	0x0D0A	Hex

Total Bytes		138			Respone will be OK

Get Display Parameter
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	6	RGETDP	ASCII
10	Display Mode	1	0 or 1	ASCII
11	End bytes	2	0x0D0A	Hex

Total Bytes		12

Response Format
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	6	RGETDP	ASCII
10	Display Mode	1	0 or 1	ASCII
11	No of Parameters	2	1 to 60	ASCII	max can be set 60
13	Display Para Ids	120	0 to FF as ASCII	ASCII	List of Ids will be provided.
					pad zero if parameters are less than 60
					to make it 120 bytes
133	Crc of Configuration	4	0 to FF	ASCII	crc of configuration para meter will start from 11th byte to 132nd bytes
					lower bytes first.
137	End bytes	2	0x0D0A	Hex

Total Bytes		138			Respone will be OK

Set Default Display
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	5	WDDDP	ASCII
9	End bytes	2	0x0D0A	Hex

Total Bytes		10			Respone will be OK

Set Bill Day
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	6	WBILLD	ASCII
10		2	"01 to 31"	ASCII
12	End bytes	2	0x0D0A	Hex

Total Bytes		13			Respone will be OK

Read Bill Day
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	6	RBILLD	ASCII
10		2	"00"	ASCII
12	End bytes	2	0x0D0A	Hex

Total Bytes		13

Response Format
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	6	RBILLD	ASCII
10		2	"01 to 31"	ASCII
12	End bytes	2	0x0D0A	Hex

Total Bytes		13

Set KNO
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	4	KNOW	ASCII
8		10		ASCII
18	End bytes	2	0x0D0A	Hex

Total Bytes		19			Respone will be OK

Get Zone Timing
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	5	RTODT	ASCII
9	End bytes	2	0x0D0A	Hex

Total Bytes		10

Response Format
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	5	RTODT	ASCII
9	Zone Info	50		ASCII
59	End bytes	2	0x0D0A	Hex

Total Bytes		60

Set Zone Timing
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE VALUE	BYTE TYPE	Remark
1	Hearder	3	EEO	ASCII
4	ID	5	WTODT	ASCII
9	Zone Info	50		ASCII
59	Crc of Configuration	4		ASCII
63	End bytes	2	0x0D0A	Hex

Total Bytes		64			Respone will be OK

## HPSEB Reading
DATA READING FORMAT

Read Serial Number-0x41
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	Serial Number	10	ASCII

Total Bytes		10

Read MFG ID-0x42
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	FW Version	16	ASCII

Total Bytes		16

Read Cummulative kWh-0x43
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	kWh	9	ASCII	(6+2)

Total Bytes		9

Read Tamper Status History-0x44
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	Month Tamper Status	3	ASCII	0-NM;1-OL;2-MAG;3-REV;4-ND;5-EARTH;6-OV;7-CO;8-LV
4	Record Seprator	1	0x1E
Total Bytes		4

Read Month kWh History-0x45
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	kWh	7	ASCII	(4+2)
8	Record Seprator	1	0x1E
Total Bytes		8

Read MD History-0x46
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	MD	5	ASCII	(2+2)
6	Field Seprator	1	0x1F
7	Date	6	"DDMMYY"
13	Field Seprator	1	0x1F
14	Time	4	"hhmm"
18	Record Seprator	1	0x1E

Total Bytes		18

Read Tamper log Info					Event Code
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	Event Code	3	ASCII
4	Field Seprator	1	0x1F
5	Voltage	5	ASCII	(3+1)
10	Field Seprator	1	0x1F
11	Effective Current	5	ASCII	(2+2)
16	Field Seprator	1	0x1F
17	Power Factor	4	ASCII	(1+2)
21	Field Seprator	1	0x1F
22	kWh	8	ASCII
30	Field Seprator	1	0x1F
31	Date	6	"DDMMYY"
37	Field Seprator	1	0x1F
38	Time	6	"hhmmss"

Total Bytes		43

Read Instant Data-0x5C
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark	UNIT
1	Voltage	5	ASCII	(3+1)	V
6	Field Seprator	1	0x1F
7	Effective Current	5	ASCII	(2+2)	A
12	Field Seprator	1	0x1F
13	Date	6	"DDMMYY"
19	Field Seprator	1	0x1F
20	Time	6	"hhmmss"
26	Field Seprator	1	0x1F
27	Power Factor	4	ASCII	(1+2)
31	Field Seprator	1	0x1F
32	Frequency	5	ASCII	(2+2)	Hz
37	Field Seprator	1	0x1F
38	Effective Power	8	ASCII	(5+2)	W
46	Field Seprator	1	0x1F
47	Apparent Power	8	ASCII	(5+2)	VA
55	Field Seprator	1	0x1F
56	Billing Count	3	ASCII
59	Field Seprator	1	0x1F
60	Self Diagnostic	1	ASCII
61	Field Seprator	1	0x1F
62	Total Tamper Count	3	ASCII

Total Bytes		60

Read LS Data-0x5D
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	Date	6	"DDMMYY"
6	Field Seprator	1	0x1F
7	Block kWh	4	ASCII	divide kWh by 100
13	Field Seprator	1	0x1F
14	Next 46 block kWh + Field Seprator	230	(ASCII+hex)
244	Last block kWh	4

Total Bytes		246

Read LS Enteries -0x5F
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	LS Enteries	4	ASCII

Total Bytes		4

Read TOD First 4 Zones-0x60
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	kWh Zone1	8	ASCII
9	Field Seprator	1	0x1F
10	kVAh Zone1	8	ASCII	divide kWh by 100
18	Field Seprator	1	0x1F	divide kVAh by 100
19	MD Zone1	4	ASCII
23	Field Seprator	1
24	Date Zone 1	6	"DDMMYY"
30	Field Seprator	1	ASCII
31	Time Zone 1	4	"hhmm"
35	Record Seprator	1	0x1E
36	Zone 2 to Zone 3	70	(ASCII+hex)
106	kWh Zone4	8	ASCII
114	Field Seprator	1
115	kVAh Zone4	8	ASCII
123	Field Seprator	1
124	MD Zone4	4	ASCII
128	Field Seprator	1
129	Date Zone 4	6	ASCII
135	Field Seprator	1
136	Time Zone 4	4	ASCII

Total Bytes		139

Read TOD Next 4 Zones-0x61
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	kWh Zone5	8	ASCII
9	Field Seprator	1	0x1F
10	kVAh Zone5	8	ASCII	divide kWh by 100
18	Field Seprator	1	0x1F	divide kVAh by 100
19	MD Zone5	4	ASCII
23	Field Seprator	1
24	Date Zone 5	6	"DDMMYY"
30	Field Seprator	1
31	Time Zone 5	4	"hhmm"
35	Record Seprator	1	0x1E
36	Zone 6 to Zone 7	70	(ASCII+hex)
106	kWh Zone8	8	ASCII
114	Field Seprator	1
115	kVAh Zone8	8	ASCII
123	Field Seprator	1
124	MD Zone8	4	ASCII
128	Field Seprator	1
129	Date Zone 8	6	ASCII
135	Field Seprator	1
136	Time Zone 8	4	ASCII

Total Bytes		139

Read Billing History-0x62
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	Bill Date	6	"DDMMYY"
7	Field Seprator	1	0x1F
8	Bill Time	4	"hhmm"	divide kWh by 100
12	Field Seprator	1	0x1F	divide kVAh by 100
13	Cummulative kWh	8	ASCII
21	Field Seprator	1
22	Cummulative kVAh	8	ASCII
30	Field Seprator	1
31	MD	4	ASCII	(2+2)
35	Field Seprator	1	0x1F
36	Date	6	"DDMMYY"
42	Field Seprator	1	0x1F
43	Time	4	"hhmm"

Total Bytes		46

Read TOD History First 4 Zones-0x63
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	kWh Zone1	8	ASCII
9	Field Seprator	1	0x1F
10	kVAh Zone1	8	ASCII	divide kWh by 100
18	Field Seprator	1	0x1F	divide kVAh by 100
19	MD Zone1	4	ASCII
23	Field Seprator	1
24	Date Zone 1	6	"DDMMYY"
30	Field Seprator	1
31	Time Zone 1	4	"hhmm"
35	Record Seprator	1	0x1E
36	Zone 2 to Zone 3	70	(ASCII+hex)
106	kWh Zone4	8	ASCII
114	Field Seprator	1
115	kVAh Zone4	8	ASCII
123	Field Seprator	1
124	MD Zone4	4	ASCII
128	Field Seprator	1
129	Date Zone 4	6	ASCII
135	Field Seprator	1
136	Time Zone 4	4	ASCII

Total Bytes		139

Read TODHistory Next 4 Zones-0x64
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	kWh Zone5	8	ASCII
9	Field Seprator	1	0x1F
10	kVAh Zone5	8	ASCII	divide kWh by 100
18	Field Seprator	1	0x1F	divide kVAh by 100
19	MD Zone5	4	ASCII
23	Field Seprator	1
24	Date Zone 5	6	"DDMMYY"
30	Field Seprator	1
31	Time Zone 5	4	"hhmm"
35	Record Seprator	1	0x1E
36	Zone 6 to Zone 7	70	(ASCII+hex)
106	kWh Zone8	8	ASCII
114	Field Seprator	1
115	kVAh Zone8	8	ASCII
123	Field Seprator	1
124	MD Zone8	4	ASCII
128	Field Seprator	1
129	Date Zone 8	6	ASCII
135	Field Seprator	1
136	Time Zone 8	4	ASCII

Total Bytes		139

Read Format Data-0x65
Byte Seq	BYTE INFO	BYTE INFO SIZE	BYTE TYPE	Remark
1	Serial Number	10	ASCII
11	Date	6	ASCII
17	Time	4	ASCII
21	MAKE	4	"EEPL"
25	KNO	10	ASCII
35	kWh	5	ASCII
40	kVAh	5	ASCII
45	kW MD	4	ASCII	(2+1)
49	Power Off Count	4	ASCII
53	Voltage	3	ASCII
56	Current	4	ASCII	(2+1)
60	Power Factor	4	ASCII	(1+2)
64	Last NM Occ Date	6	"DDMMYY"
70	Last NM Res Date	4	"hhmm"
74	Last MAG OCC Date	6	"DDMMYY"
80	Last MAG Res Date	4	"hhmm"
84	Last REV OCC Date	6	"DDMMYY"
90	Last REV Res Date	4	"hhmm"
94	Last ND OCC Date	6	"DDMMYY"
100	Last ND Res Date	4	"hhmm"
104	Last EARTH OCC Date	6	"DDMMYY"
110	Last EARTH Res Date	4	"hhmm"
114	Last CO OCC Date	6	"DDMMYY"
120	Last CO Res Date	4	"hhmm"

Total Bytes		123

## Display IDs
Parameter Name	Decimal Point	Unit	ID
kWh without decimal	0	kWh	0x00
Voltage	1	V	0x01
Phase Current	3	A	0x02
Neutral Current	3	A	0x03
Effective Current	3	A	0x04
Phase Power	2	W	0x05
Neutral Power	2	W	0x06
Effective Power	2	W	0x07
Apparent Power	2	VA	0x08
Pf	2		0x09
Frequrency	2	Hz	0x0A
Current Time			0x0B
Current Date			0x0C
Current Month MD	2	kW	0x0D
Current Month Time			0x0E
Current Month Date			0x0F
High kWh	4	kWh	0x10
Phase Power kW	2	kW	0x12
Neutral Power kW	2	kW	0x13
Effect. Power kW	2	kW	0x14
kVAh	0	kVAh	0x15
Current Month MD	2	kVA	0x16
Current Month Time			0x17
Current Month Date			0x18
High kVAh	4	kVAh	0z19
Cum. Power On Hour			0x1E
Cum. MD	2	kW	0x1F
Billing Count			0x20
Cum. MD	2	kVA	0x21
kWh	1	kWh	0x22
Main BAT Status			0x27
Serial Number			0x3F
H1 MD	2	kW	0x40
H1 MD Time			0x41
H1 MD Date			0x42
H1 kWh	2	kWh	0x43
H1 Avg Pf	2		0x44
H2 MD	2	kW	0x45
H2 MD Time			0x46
H2 MD Date			0x47
H2 kWh	2	kWh	0x48
H2 Avg Pf	2		0x49
H3 MD	2	kW	0x4A
H3 MD Time			0x4B
H3 MD Date			0x4C
H3 kWh	2	kWh	0x4D
H3 Avg Pf	2		0x4E
H4 MD	2	kW	0x4F
H4 MD Time			0x50
H4 MD Date			0x51
H4 kWh	2	kWh	0x52
H4 Avg Pf	2		0x53
H5 MD	2	kW	0x54
H5 MD Time			0x55
H5 MD Date			0x56
H5 kWh	2	kWh	0x57
H5 Avg Pf	2		0x58
H6 MD	2	kW	0x59
H6 MD Time			0x5A
H6 MD Date			0x5B
H6 kWh	2	kWh	0x5C
H6 Avg Pf	2		0x5D
Total Tamper Count			0x6E
Current Avg. Pf	2		0x6F
H1 kVAh	0	kAVh	0x80
H2 kVAh	0	kAVh	0x81
H3 kVAh	0	kAVh	0x82
H4 kVAh	0	kAVh	0x83
H5 kVAh	0	kAVh	0x84
H6 kVAh	0	kAVh	0x85
Rtc Bat Status			0x90
NVM Status			0x91
H1 Power On Hour			0x95